## Summary Sheet
SEER and SCOP values for FUJITSU J-II Heat Pump Systems Revised April 2015
Model | Description | EER | *SEER | COP | SCOP
AJYA40LALH | 4HP Heat Pump | 3.72 | 5.5121 | 4.29 | 4.6467
AJYA45LALH | 5HP Heat Pump | 3.6 | 5.5478 | 4.2 | 4.8351
AJYA54LALH | 6HP Heat Pump | 3.45 | 5.4727 | 3.95 | 4.8937
* SEER values based on a General Office Type Accommodation load profile as detailed in section 9 of the Non-Domestic Heating, Cooling and Ventilation Compliance Guide

## J-II SEER
FUJITSU J-II VRF SYSTEM
SEER DATA
Enter required quantities to reveal individual or cumulative results | [11 empty] | Data Input
[5 empty] | Cooling | [5 empty] | Cooling
| Model | Description | QTY | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ |  | Nom Clg kW | 25% @ 20℃ | 50% @ 25℃ | 75% @ 30℃ | 100% @ 35℃ | SEER
|  |  |  | Nom PI | [5 empty] | Nom PI
[5 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe J-II Heat Pump | AJYA40LALH | 4HP Heat Pump | [7 empty] | 12.1 | 3.03 | 6.05 | 9.08 | 12.1 | 5.5121
[10 empty] | 3.25 | 0.68 | 0.88 | 1.71 | 3.25
| AJYA45LALH | 5HP Heat Pump | [7 empty] | 14 | 3.5 | 7 | 10.5 | 14 | 5.5478
[10 empty] | 3.89 | 0.65 | 1.05 | 2.05 | 3.89
| AJYA54LALH | 6HP Heat Pump | [7 empty] | 15.5 | 3.88 | 7.75 | 11.63 | 15.5 | 5.4727
[10 empty] | 4.49 | 0.66 | 1.21 | 2.36 | 4.49
| Total Project (VRF) Cooling Output |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  | 0 | 0 | 0 | 0 | 0
| Overall Energy Efficiency Ratio |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SEER
| Load Profile - Unknown |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!

## J-II SCOP
FUJITSU J-II VRF SYSTEMS
SCOP DATA
Revised April 2015
Enter required quantities to reveal individual or cumulative results |  |  |  |  | Heating | [5 empty] | Heating
| Model | Description | QTY | Nom Htg kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ |  | Nom HTG kW | 25% @ 15℃ | 50% @ 7℃ | 75% @ 1℃ | 100% @ -5℃ | SEER
|  |  |  | Nom PI | [5 empty] | Nom PI
[5 empty] | 0.25 | 0.5 | 0.75 | 1 |  |  | 0.25 | 0.5 | 0.75 | 1
2-pipe J-II Mini VRF Heat Pump | AJYA40LALH | 4HP Heat Pump | [7 empty] | 13.6 | 3.4 | 6.8 | 10.2 | 13.6 | 4.6467
[10 empty] | 3.17 | 0.91 | 1.18 | 2.28 | 4.15
| AJYA45LALH | 5HP Heat Pump | [7 empty] | 16 | 4 | 8 | 12 | 15.5 | 4.8351
[10 empty] | 3.81 | 0.87 | 1.39 | 2.71 | 4.36
| AJYA54LALH | 6HP Heat Pump | [7 empty] | 18 | 4.5 | 9 | 13.2 | 16 | 4.8937
[10 empty] | 4.56 | 0.9 | 1.57 | 3 | 4.55
| Total Project (VRF) Cooling Output |  |  | 0 | 0 | 0 | 0 | 0
| Total Compressor & Outdoor Fan Power Consumption |  |  | 0 | 0 | 0 | 0 | 0
| Overall COP |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SCOP
| Load Profile - Unknown |  |  |  | 25% | 25% | 25% | 25% | #DIV/0!
| Load Profile - General Office Type Accommodation |  |  |  | 20% | 36% | 32% | 12% | #DIV/0!
| Load Profile - User Defined |  |  |  | 0% | 0% | 0% | 0% | #DIV/0!